## Voltage Drop
Calculate Cable Voltage Drop for Different Size of Cables | [6 empty] | Starting Voltage Regulation: |  |  |  | 3.291%
Jignesh.Parmar www.electricalnotes.wordpress.com | [6 empty] | Running Voltage Regulation: |  |  |  | 2.658%
|  |  |  | 350 | [9 empty] | 277 |  | 297.9827 | 560.0329 | 858.0155 | 419.7301 | 13.915 | 3.291% | 11.1797 | 2.658%
Cable Route |  | Cable Length |  |  | Cable Details |  |  |  | Load Detail | [10 empty] | Starting Condition |  | Running Condition
From | to | Length (Mt) | No. of Cable / Run | Total Length (Mt) | Size of Cables | Type of Cond. | Res.of Cable (R) (Ω/Km) | Rea.of Cable (X) (Ω/Km) | Supply Voltage | Starting P.F | Running P.F | Lighting Load (Kw) | Motor Load (Kw) | Total Load (Kw) | Motor Lock Rotor Current | Starting Current of Ltg Load | Starting Current of Motor Load | Total Starting Current | Full Load Current (Amp) | Voltage drop (Volt) | % Regulaton | Voltage drop (Volt) | % Regulaton
USS | Panel-A | 50 | 2 | 100 | 3cX 300 Sq.mm LT XLPE (Up to 1.1KV) | ALU | 0.13 | 0.071 | 433 | 0.6 | 0.9 |  | 126 | 126 | 3 | 0 | 560.0329 | 560.0329 | 186.6776 | 3.2688 | 0.7549% | 1.1959 | 0.2762% | 2 | 0.13 | 0.071 | 0.9 | 0.43589 | 0.6 | 0.8
Panel-A | Panel-B | 100 | 2 | 200 | 3.5X300Sq.mm LT XLPE (Up to 1.1KV) | ALU | 0.13 | 0.071 | 433 | 0.7 | 0.9 | 126 |  | 126 | 3 | 240.0141 | 0 | 240.0141 | 186.6776 | 2.9454 | 0.6802% | 2.3918 | 0.5524% | 2 | 0.13 | 0.071 | 0.9 | 0.43589 | 0.7 | 0.71414
Panel-B | Panel-C | 50 | 1 | 50 | 4cX16 Sq.mm LT XLPE (Up to 1.1KV) | ALU | 2.45 | 0.08 | 415 | 0.6 | 0.75 | 25 |  | 25 | 2 | 57.9686 | 0 | 57.9686 | 46.3749 | 7.7008 | 1.856% | 7.592 | 1.829% | 2 | 2.45 | 0.08 | 0.75 | 0.66144 | 0.6 | 0.8
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1
|  |  |  | 0 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 4 |  |  | 0 | 1 | 0 | 1

## Cable Detail
Nominal Conductor Area (Sq.mm) | Aluminium |  | Copper |  | Aluminum | Copper | Short Circuit Current Rating for 1Sec.duration in K. Amps |  | ALU | 2
| Resi | React | Resi | React | Air | Air | Aluminium | Copper | CU | 4
| Ω/km | Ω/km | Ω/km | Ω/km | Amp | Amp
1cX4Sq.mm LT PVC (Up to 1.1KV) | 8.8 | 0.158 | 5.52 | 0.0158 | — | 35 | 0.304 | 0.460
1cX6Sq.mm LT PVC (Up to 1.1KV) | 5.53 | 0.148 | 3.69 | 0.148 | 35 | 44 | 0.456 | 0.690
1cX10Sq.mm LT PVC (Up to 1.1KV) | 3.7 | 0.138 | 2.19 | 0.138 | 47 | 60 | 0.760 | 1.150
1cX16Sq.mm LT PVC (Up to 1.1KV) | 2.29 | 0.128 | 1.38 | 0.128 | 64 | 82 | 1.220 | 1.84
1cX25Sq.mm LT PVC (Up to 1.1KV) | 1.44 | 0.12 | 0.87 | 0.12 | 84 | 110 | 1.900 | 2.88
1cX35Sq.mm LT PVC (Up to 1.1KV) | 1.04 | 0.114 | 0.627 | 0.114 | 105 | 130 | 2.660 | 4.03
1cX50Sq.mm LT PVC (Up to 1.1KV) | 0.77 | 0.11 | 0.463 | 0.11 | 130 | 165 | 3.8 | 5.75
1cX70Sq.mm LT PVC (Up to 1.1KV) | 0.53 | 0.103 | 0.321 | 0.103 | 155 | 205 | 5.320 | 8.05
1cX95Sq.mm LT PVC (Up to 1.1KV) | 0.38 | 0.101 | 0.231 | 0.101 | 190 | 245 | 7.220 | 10.90
1cX120Sq.mm LT PVC (Up to 1.1KV) | 0.3 | 0.096 | 0.184 | 0.096 | 220 | 280 | 9.120 | 13.80
1cX150 Sq.mm LT PVC (Up to 1.1KV) | 0.25 | 0.094 | 0.149 | 0.094 | 250 | 320 | 11.40 | 17.30
1cX185 Sq.mm LT PVC (Up to 1.1KV) | 0.2 | 0.092 | 0.12 | 0.092 | 290 | 370 | 14.10 | 21.30
1cX240 Sq.mm LT PVC (Up to 1.1KV) | 0.15 | 0.09 | 0.091 | 0.09 | 335 | 425 | 18.20 | 27.30
1cX300 Sq.mm LT PVC (Up to 1.1KV) | 0.12 | 0.088 | 0.074 | 0.088 | 380 | 475 | 22.8 | 34.50
1cX400 Sq.mm LT PVC (Up to 1.1KV) | 0.094 | 0.088 | 0.059 | 0.088 | 435 | 550 | 30.40 | 46.00
1cX 500 Sq.mm LT PVC (Up to 1.1KV) | 0.0726 | 0.087 | 0.046 | 0.087 | 480 | 590 | 38.00 | 57.50
1cX 630 Sq.mm LT PVC (Up to 1.1KV) | 0.0563 | 0.086 | 0.037 | 0.086 | 550 | 660 | 47.90 | 72.50
1cX800 Sq.mm LT PVC (Up to 1.1KV) | 0.044 | 0.083 | 0.031 | 0.083 | 610 | 725 | 60.80 | 92.00
1cX1000 Sq.mm LT PVC (Up to 1.1KV) | 0.0349 | 0.082 | 0.027 | 0.082 | 680 | 870 | 76.00 | 115.00
2cX1.5Sq.mm LT PVC (Up to 1.1KV) | 21.72 | 0.126 | 14.5 | 0.126 | 16 | 20 | 0.3 | 0.4
2cX2.5Sq.mm LT PVC (Up to 1.1KV) | 14.52 | 0.119 | 8.87 | 0.119 | 21 | 27 | 0.3 | 0.4
2cX4Sq.mm LT PVC (Up to 1.1KV) | 8.89 | 0.116 | 5.52 | 0.116 | 27 | 35 | 0.304 | 0.460
2cX 6 Sq.mm LT PVC (Up to 1.1KV) | 5.53 | 0.11 | 3.69 | 0.11 | 35 | 45 | 0.456 | 0.690
2cX10 Sq.mm LT PVC (Up to 1.1KV) | 3.7 | 0.1 | 2.19 | 0.1 | 47 | 60 | 0.760 | 1.150
2cX16 Sq.mm LT PVC (Up to 1.1KV) | 2.29 | 0.097 | 1.38 | 0.097 | 59 | 78 | 1.220 | 1.840
2cX25 Sq.mm LT PVC (Up to 1.1KV) | 1.44 | 0.097 | 0.87 | 0.097 | 78 | 105 | 1.900 | 2.880
2cX35 Sq.mm LT PVC (Up to 1.1KV) | 1.04 | 0.097 | 0.627 | 0.097 | 99 | 125 | 2.660 | 4.030
2cX50 Sq.mm LT PVC (Up to 1.1KV) | 0.77 | 0.094 | 0.463 | 0.094 | 125 | 155 | 3.800 | 5.750
2cX70 Sq.mm LT PVC (Up to 1.1KV) | 0.53 | 0.09 | 0.321 | 0.09 | 150 | 195 | 5.320 | 8.050
2cX95 Sq.mm LT PVC (Up to 1.1KV) | 0.38 | 0.09 | 0.231 | 0.9 | 185 | 230 | 7.220 | 10.90
2cX120 Sq.mm LT PVC (Up to 1.1KV) | 0.3 | 0.087 | 0.184 | 0.087 | 210 | 265 | 9.120 | 13.80
2cX150 Sq.mm LT PVC (Up to 1.1KV) | 0.25 | 0.087 | 0.149 | 0.087 | 240 | 305 | 11.40 | 17.300
2cX185 Sq.mm LT PVC (Up to 1.1KV) | 0.2 | 0.087 | 0.12 | 0.087 | 275 | 350 | 14.10 | 21.280
2cX240 Sq.mm LT PVC (Up to 1.1KV) | 0.15 | 0.087 | 0.091 | 0.087 | 325 | 410 | 18.20 | 27.600
2cX300 Sq.mm LT PVC (Up to 1.1KV) | 0.12 | 0.086 | 0.073 | 0.086 | 365 | 465 | 22.80 | 34.500
2cX400 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.059 | 0.086 | 420 | 530 | 30.40 | 46.000
2cX500 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.059 | 0.086 | 475 | 605 | 38.00 | 57.500
2cX630 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.059 | 0.086 | 540 | 785 | 47.90 | 72.550
3cX1.5Sq.mm LT PVC (Up to 1.1KV) | 21.72 | 0.126 | 14.5 | 0.126 | 13 | 17 | 0.3 | 0.4
3cX2.5Sq.mm LT PVC (Up to 1.1KV) | 14.52 | 0.119 | 8.87 | 0.119 | 18 | 24 | 0.3 | 0.4
3cX4Sq.mm LT PVC (Up to 1.1KV) | 8.89 | 0.116 | 5.52 | 0.116 | 23 | 30 | 0.304 | 0.460
3cX 6 Sq.mm LT PVC (Up to 1.1KV) | 5.53 | 0.11 | 3.69 | 0.11 | 30 | 39 | 0.456 | 0.690
3cX 10 Sq.mm LT PVC (Up to 1.1KV) | 3.7 | 0.1 | 2.19 | 0.1 | 40 | 52 | 0.760 | 1.150
3cX 16 Sq.mm LT PVC (Up to 1.1KV) | 2.29 | 0.097 | 1.38 | 0.097 | 51 | 66 | 1.220 | 1.840
3cX 25 Sq.mm LT PVC (Up to 1.1KV) | 1.44 | 0.097 | 0.87 | 0.097 | 70 | 90 | 1.900 | 2.880
3cX 35 Sq.mm LT PVC (Up to 1.1KV) | 1.04 | 0.097 | 0.627 | 0.097 | 86 | 110 | 2.660 | 4.030
3cX 50 Sq.mm LT PVC (Up to 1.1KV) | 0.77 | 0.094 | 0.463 | 0.094 | 105 | 135 | 3.800 | 5.750
3cX 70 Sq.mm LT PVC (Up to 1.1KV) | 0.53 | 0.09 | 0.321 | 0.09 | 130 | 165 | 5.320 | 8.050
3cX 95 Sq.mm LT PVC (Up to 1.1KV) | 0.38 | 0.9 | 0.231 | 0.09 | 155 | 200 | 7.220 | 10.900
3cX 120 Sq.mm LT PVC (Up to 1.1KV) | 0.3 | 0.087 | 0.184 | 0.087 | 180 | 230 | 9.120 | 13.800
3cX 150 Sq.mm LT PVC (Up to 1.1KV) | 0.25 | 0.087 | 0.149 | 0.087 | 205 | 265 | 11.40 | 17.300
3cX 185 Sq.mm LT PVC (Up to 1.1KV) | 0.2 | 0.087 | 0.12 | 0.087 | 240 | 305 | 14.10 | 21.300
3cX 240 Sq.mm LT PVC (Up to 1.1KV) | 0.15 | 0.087 | 0.0912 | 0.087 | 280 | 355 | 18.20 | 27.600
3cX 300 Sq.mm LT PVC (Up to 1.1KV) | 0.12 | 0.086 | 0.0739 | 0.086 | 315 | 400 | 22.80 | 34.500
3cX 400 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.0592 | 0.086 | 375 | 435 | 30.40 | 46.000
3cX 500 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.0592 | 0.086 | 425 | 520 | 38.00 | 57.500
3cX 630 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.0592 | 0.086 | 480 | 675 | 47.90 | 72.500
3.5X16Sq.mm LT PVC (Up to 1.1KV) | 1.44 | 0.097 | 0.73 | 0.097 | 62 | 90 | 1.8 | 2.5
3.5X25Sq.mm LT PVC (Up to 1.1KV) | 0.77 | 0.094 | 0.387 | .0.094 | 70 | 90 | 1.90 | 2.88
3.5X35Sq.mm LT PVC (Up to 1.1KV) | 0.53 | 0.09 | 0.268 | 0.09 | 86 | 110 | 2.66 | 4.03
3.5X50Sq.mm LT PVC (Up to 1.1KV) | 0.38 | 0.09 | 0.193 | 0.09 | 105 | 135 | 3.80 | 5.75
3.5X70Sq.mm LT PVC (Up to 1.1KV) | 0.3 | 0.087 | 0.153 | 0.087 | 130 | 165 | 5.32 | 8.05
3.5X95Sq.mm LT PVC (Up to 1.1KV) | 0.2 | 0.087 | 0.099 | 0.087 | 155 | 200 | 7.22 | 10.90
3.5X120Sq.mm LT PVC (Up to 1.1KV) | 0.15 | 0.087 | 0.075 | 0.087 | 180 | 230 | 9.12 | 13.80
3.5X150Sq.mm LT PVC (Up to 1.1KV) | 0.12 | 0.086 | 0.06 | 0.086 | 205 | 265 | 11.40 | 17.30
3.5X185Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.047 | 0.086 | 240 | 305 | 14.10 | 21.30
3.5X240Sq.mm LT PVC (Up to 1.1KV) | 0.08 | 0.085 | 0.046 | 0.085 | 280 | 355 | 18.20 | 27.60
3.5X300Sq.mm LT PVC (Up to 1.1KV) | 0.08 | 0.085 | 0.046 | 0.085 | 315 | 400 | 22.80 | 34.50
3.5X400Sq.mm LT PVC (Up to 1.1KV) | 0.08 | 0.084 | 0.045 | 0.084 | 375 | 435 | 30.40 | 46.00
3.5X500Sq.mm LT PVC (Up to 1.1KV) | 0.08 | 0.084 | 0.045 | 0.084 | 425 | 520 | 38.00 | 57.50
3.5X630Sq.mm LT PVC (Up to 1.1KV) | 0.08 | 0.084 | 0.045 | 0.084 | 480 | 675 | 47.90 | 72.50
4cX 1.5Sq.mm LT PVC (Up to 1.1KV) | 21.72 | 0.126 | 14.5 | 0.126 | 13 | 17 | 0.3 | 0.4
4cX 2.5Sq.mm LT PVC (Up to 1.1KV) | 14.52 | 0.119 | 8.87 | 0.119 | 18 | 24 | 0.3 | 0.4
4cX4 Sq.mm LT PVC (Up to 1.1KV) | 8.89 | 0.116 | 5.52 | 0.116 | 23 | 30 | 0.304 | 0.460
4cX 6 Sq.mm LT PVC (Up to 1.1KV) | 5.53 | 0.11 | 3.69 | 0.11 | 30 | 39 | 0.456 | 0.690
4cX 10 Sq.mm LT PVC (Up to 1.1KV) | 3.7 | 0.1 | 2.19 | 0.1 | 40 | 52 | 0.760 | 1.150
4cX16 Sq.mm LT PVC (Up to 1.1KV) | 2.29 | 0.097 | 1.38 | 0.097 | 51 | 66 | 1.220 | 1.840
4cX 25 Sq.mm LT PVC (Up to 1.1KV) | 1.44 | 0.097 | 0.87 | 0.097 | 70 | 90 | 1.900 | 2.880
4cX35 Sq.mm LT PVC (Up to 1.1KV) | 1.04 | 0.097 | 0.62 | 0.097 | 86 | 110 | 2.660 | 4.030
4cX 50 Sq.mm LT PVC (Up to 1.1KV) | 0.77 | 0.094 | 0.46 | 0.094 | 105 | 135 | 3.800 | 5.750
4cX70 Sq.mm LT PVC (Up to 1.1KV) | 0.53 | 0.09 | 0.32 | 0.09 | 130 | 165 | 5.320 | 8.050
4cX 95 Sq.mm LT PVC (Up to 1.1KV) | 0.38 | 0.09 | 0.23 | 0.09 | 155 | 200 | 7.220 | 10.900
4cX 120 Sq.mm LT PVC (Up to 1.1KV) | 0.3 | 0.087 | 0.18 | 0.087 | 180 | 230 | 9.120 | 13.800
4cX 150 Sq.mm LT PVC (Up to 1.1KV) | 0.25 | 0.087 | 0.14 | 0.087 | 205 | 265 | 11.400 | 17.300
4cX 185 Sq.mm LT PVC (Up to 1.1KV) | 0.2 | 0.087 | 0.12 | 0.087 | 240 | 305 | 14.100 | 21.300
4cX 240 Sq.mm LT PVC (Up to 1.1KV) | 0.15 | 0.087 | 0.091 | 0.087 | 280 | 355 | 18.200 | 27.600
4cX 300 Sq.mm LT PVC (Up to 1.1KV) | 0.12 | 0.086 | 0.073 | 0.086 | 315 | 400 | 22.800 | 34.500
4cX 400 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.059 | 0.086 | 375 | 435 | 30.400 | 46.000
4cX 500 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.059 | 0.086 | 425 | 520 | 38.000 | 57.500
4cX 630 Sq.mm LT PVC (Up to 1.1KV) | 0.09 | 0.086 | 0.059 | 0.086 | 480 | 675 | 47.900 | 72.500
1cX4Sq.mm LT XLPE (Up to 1.1KV) | 1.555 | 0.102 | 1.555 | 0.102 | — | 45 | 0.376 | 0.572
1cX6Sq.mm LT XLPE (Up to 1.1KV) | 1.553 | 0.102 | 1.553 | 0.102 | 45 | 57 | 0.564 | 0.858
1cX10Sq.mm LT XLPE (Up to 1.1KV) | 1.553 | 0.102 | 1.553 | 0.102 | 61 | 77 | 0.940 | 1.430
1cX16Sq.mm LT XLPE (Up to 1.1KV) | 1.54 | 0.102 | 1.54 | 0.102 | 83 | 106 | 1.504 | 2.288
1cX25Sq.mm LT XLPE (Up to 1.1KV) | 1.54 | 0.102 | 0.93 | 0.102 | 115 | 145 | 2.350 | 3.575
1cX35Sq.mm LT XLPE (Up to 1.1KV) | 1.11 | 0.097 | 0.671 | 0.097 | 135 | 175 | 3.290 | 5.005
1cX50Sq.mm LT XLPE (Up to 1.1KV) | 0.82 | 0.092 | 0.495 | 0.092 | 170 | 215 | 4.700 | 7.150
1cX70Sq.mm LT XLPE (Up to 1.1KV) | 0.56 | 0.088 | 0.343 | 0.088 | 210 | 270 | 6.580 | 10.01
1cX95Sq.mm LT XLPE (Up to 1.1KV) | 0.41 | 0.085 | 0.247 | 0.085 | 255 | 330 | 8.930 | 13.59
1cX120Sq.mm LT XLPE (Up to 1.1KV) | 0.32 | 0.082 | 0.196 | 0.082 | 300 | 380 | 11.28 | 17.16
1cX150 Sq.mm LT XLPE (Up to 1.1KV) | 0.265 | 0.082 | 0.159 | 0.082 | 342 | 430 | 14.10 | 21.45
1cX185 Sq.mm LT XLPE (Up to 1.1KV) | 0.211 | 0.082 | 0.127 | 0.082 | 385 | 495 | 17.39 | 26.46
1cX240 Sq.mm LT XLPE (Up to 1.1KV) | 0.162 | 0.079 | 0.0965 | 0.079 | 450 | 590 | 22.56 | 34.32
1cX300 Sq.mm LT XLPE (Up to 1.1KV) | 0.13 | 0.078 | 0.0769 | 0.078 | 519 | 670 | 28.20 | 42.90
1cX400 Sq.mm LT XLPE (Up to 1.1KV) | 0.1023 | 0.077 | 0.0608 | 0.077 | 605 | 780 | 37.60 | 57.20
1cX 500 Sq.mm LT XLPE (Up to 1.1KV) | 0.0808 | 0.076 | 0.0468 | 0.076 | 700 | 900 | 47.00 | 71.50
1cX 630 Sq.mm LT XLPE (Up to 1.1KV) | 0.0648 | 0.075 | 0.0362 | 0.075 | 809 | 1020 | 59.22 | 90.09
1cX800 Sq.mm LT XLPE (Up to 1.1KV) | 0.053 | 0.075 | 0.0283 | 0.075 | 935 | 1140 | 75.20 | 114.40
1cX1000 Sq.mm LT XLPE (Up to 1.1KV) | 0.0444 | 0.068 | 0.0225 | 0.068 | 1065 | 1250 | 94.00 | 143.00
2cX1.5Sq.mm LT XLPE (Up to 1.1KV) | — | — | — | — | — | — | — | —
2cX2.5Sq.mm LT XLPE (Up to 1.1KV) | — | — | — | — | — | — | — | —
2cX4Sq.mm LT XLPE (Up to 1.1KV) | 1.555 | 0.097 | 1.555 | 0.097 | 30 | 39 | 0.376 | 0.572
2cX 6 Sq.mm LT XLPE (Up to 1.1KV) | 1.553 | 0.097 | 1.553 | 0.097 | 40 | 50 | 0.564 | 0.858
2cX10 Sq.mm LT XLPE (Up to 1.1KV) | 1.553 | 0.085 | 1.553 | 0.085 | 53 | 67 | 0.940 | 1.430
2cX16 Sq.mm LT XLPE (Up to 1.1KV) | 1.54 | 0.08 | 1.54 | 0.08 | 70 | 85 | 1.50 | 2.29
2cX25 Sq.mm LT XLPE (Up to 1.1KV) | 1.54 | 0.08 | 0.93 | 0.08 | 99 | 125 | 2.35 | 3.58
2cX35 Sq.mm LT XLPE (Up to 1.1KV) | 1.11 | 0.08 | 0.671 | 0.08 | 117 | 155 | 3.29 | 5.01
2cX50 Sq.mm LT XLPE (Up to 1.1KV) | 0.082 | 0.078 | 0.495 | 0.078 | 140 | 190 | 4.70 | 7.15
2cX70 Sq.mm LT XLPE (Up to 1.1KV) | 0.57 | 0.077 | 0.343 | 0.077 | 176 | 235 | 6.58 | 10.01
2cX95 Sq.mm LT XLPE (Up to 1.1KV) | 0.41 | 0.074 | 0.247 | 0.074 | 221 | 290 | 8.93 | 13.59
2cX120 Sq.mm LT XLPE (Up to 1.1KV) | 0.33 | 0.072 | 0.196 | 0.072 | 258 | 330 | 11.28 | 17.16
2cX150 Sq.mm LT XLPE (Up to 1.1KV) | 0.27 | 0.072 | 0.159 | 0.072 | 294 | 375 | 14.10 | 21.45
2cX185 Sq.mm LT XLPE (Up to 1.1KV) | 0.21 | 0.072 | 0.127 | 0.072 | 339 | 435 | 17.39 | 26.46
2cX240 Sq.mm LT XLPE (Up to 1.1KV) | 0.16 | 0.072 | 0.0965 | 0.072 | 402 | 510 | 22.56 | 34.32
2cX300 Sq.mm LT XLPE (Up to 1.1KV) | 0.13 | 0.071 | 0.0769 | 0.071 | 461 | 590 | 28.20 | 42.90
2cX400 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 542 | 670 | 37.60 | 57.20
2cX500 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 624 | 750 | 47.00 | 71.50
2cX630 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 723 | 875 | 59.22 | 90.09
3cX1.5Sq.mm LT XLPE (Up to 1.1KV) | — | — | — | — | — | — | — | —
3cX2.5Sq.mm LT XLPE (Up to 1.1KV) | — | — | — | — | — | — | — | —
3cX4Sq.mm LT XLPE (Up to 1.1KV) | 1.581 | 0.097 | 1.581 | 0.097 | 30 | 39 | 0.376 | 0.572
3cX 6 Sq.mm LT XLPE (Up to 1.1KV) | 1.57 | 0.097 | 1.57 | 0.097 | 40 | 50 | 0.564 | 0.858
3cX 10 Sq.mm LT XLPE (Up to 1.1KV) | 1.55 | 0.08 | 1.55 | 0.08 | 53 | 67 | 0.940 | 1.430
3cX 16 Sq.mm LT XLPE (Up to 1.1KV) | 1.557 | 0.08 | 1.557 | 0.08 | 70 | 85 | 1.50 | 2.29
3cX 25 Sq.mm LT XLPE (Up to 1.1KV) | 1.54 | 0.08 | 0.93 | 0.08 | 99 | 125 | 2.35 | 3.58
3cX 35 Sq.mm LT XLPE (Up to 1.1KV) | 1.11 | 0.08 | 0.671 | 0.08 | 117 | 155 | 3.29 | 5.01
3cX 50 Sq.mm LT XLPE (Up to 1.1KV) | 0.82 | 0.78 | 0.495 | 0.078 | 140 | 190 | 4.70 | 7.15
3cX 70 Sq.mm LT XLPE (Up to 1.1KV) | 0.57 | 0.077 | 0.343 | 0.077 | 176 | 235 | 6.58 | 10.01
3cX 95 Sq.mm LT XLPE (Up to 1.1KV) | 0.41 | 0.074 | 0.247 | 0.074 | 221 | 290 | 8.93 | 13.59
3cX 120 Sq.mm LT XLPE (Up to 1.1KV) | 0.33 | 0.072 | 0.196 | 0.072 | 258 | 330 | 11.28 | 17.16
3cX 150 Sq.mm LT XLPE (Up to 1.1KV) | 0.27 | 0.072 | 0.159 | 0.072 | 294 | 375 | 14.10 | 21.45
3cX 185 Sq.mm LT XLPE (Up to 1.1KV) | 0.21 | 0.072 | 0.127 | 0.072 | 339 | 435 | 17.39 | 26.46
3cX 240 Sq.mm LT XLPE (Up to 1.1KV) | 0.16 | 0.072 | 0.0965 | 0.072 | 402 | 510 | 22.56 | 34.32
3cX 300 Sq.mm LT XLPE (Up to 1.1KV) | 0.13 | 0.071 | 0.0769 | 0.071 | 461 | 590 | 28.20 | 42.90
3cX 400 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 542 | 670 | 37.60 | 57.20
3cX 500 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 624 | 750 | 47.00 | 71.50
3cX 630 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 723 | 875 | 59.22 | 90.09
3.5X16Sq.mm LT XLPE (Up to 1.1KV) | — | — | — | — | — | — | — | —
3.5X25Sq.mm LT XLPE (Up to 1.1KV) | 1.54 | 0.08 | 0.93 | 0.08 | 99 | 125 | 2.35 | 3.58
3.5X35Sq.mm LT XLPE (Up to 1.1KV) | 1.11 | 0.08 | 0.671 | 0.08 | 117 | 155 | 3.29 | 5.01
3.5X50Sq.mm LT XLPE (Up to 1.1KV) | 0.82 | 0.078 | 0.0495 | 0.078 | 140 | 190 | 4.70 | 7.15
3.5X70Sq.mm LT XLPE (Up to 1.1KV) | 0.57 | 0.077 | 0.343 | 0.077 | 176 | 235 | 6.58 | 10.01
3.5X95Sq.mm LT XLPE (Up to 1.1KV) | 0.41 | 0.074 | 0.247 | 0.074 | 221 | 290 | 8.93 | 13.59
3.5X120Sq.mm LT XLPE (Up to 1.1KV) | 0.33 | 0.072 | 0.196 | 0.072 | 258 | 330 | 11.28 | 17.16
3.5X150Sq.mm LT XLPE (Up to 1.1KV) | 0.27 | 0.072 | 0.159 | 0.072 | 294 | 375 | 14.10 | 21.45
3.5X185Sq.mm LT XLPE (Up to 1.1KV) | 0.21 | 0.072 | 0.127 | 0.072 | 339 | 435 | 17.39 | 26.46
3.5X240Sq.mm LT XLPE (Up to 1.1KV) | 0.16 | 0.072 | 0.0965 | 0.072 | 402 | 510 | 22.56 | 34.32
3.5X300Sq.mm LT XLPE (Up to 1.1KV) | 0.13 | 0.071 | 0.0769 | 0.071 | 461 | 590 | 28.20 | 42.90
3.5X400Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 542 | 670 | 37.60 | 57.20
3.5X500Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 624 | 750 | 47.00 | 71.50
3.5X630Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 723 | 875 | 59.22 | 90.09
4cX 1.5Sq.mm LT XLPE (Up to 1.1KV) | — | — | — | — | — | — | — | —
4cX 2.5Sq.mm LT XLPE (Up to 1.1KV) | — | — | — | — | — | — | — | —
4cX4 Sq.mm LT XLPE (Up to 1.1KV) | 5.53 | 0.11 | 3.69 | 0.11 | 30 | 39 | 0.376 | 0.572
4cX 6 Sq.mm LT XLPE (Up to 1.1KV) | 3.7 | 0.1 | 2.19 | 0.1 | 40 | 50 | 0.564 | 0.858
4cX 10 Sq.mm LT XLPE (Up to 1.1KV) | 2.29 | 0.097 | 1.38 | 0.097 | 53 | 67 | 0.940 | 1.430
4cX16 Sq.mm LT XLPE (Up to 1.1KV) | 2.45 | 0.08 | 1.47 | 0.08 | 70 | 85 | 1.50 | 2.29
4cX 25 Sq.mm LT XLPE (Up to 1.1KV) | 1.54 | 0.08 | 0.93 | 0.08 | 99 | 125 | 2.35 | 3.58
4cX35 Sq.mm LT XLPE (Up to 1.1KV) | 1.11 | 0.08 | 0.671 | 0.08 | 117 | 155 | 3.29 | 5.01
4cX 50 Sq.mm LT XLPE (Up to 1.1KV) | 0.082 | 0.078 | 0.495 | 0.078 | 140 | 190 | 4.70 | 7.15
4cX70 Sq.mm LT XLPE (Up to 1.1KV) | 0.57 | 0.077 | 0.343 | 0.077 | 176 | 235 | 6.58 | 10.01
4cX 95 Sq.mm LT XLPE (Up to 1.1KV) | 0.41 | 0.074 | 0.247 | 0.074 | 221 | 290 | 8.93 | 13.59
4cX 120 Sq.mm LT XLPE (Up to 1.1KV) | 0.33 | 0.072 | 0.196 | 0.072 | 258 | 330 | 11.28 | 17.16
4cX 150 Sq.mm LT XLPE (Up to 1.1KV) | 0.27 | 0.072 | 0.159 | 0.072 | 294 | 375 | 14.10 | 21.45
4cX 185 Sq.mm LT XLPE (Up to 1.1KV) | 0.21 | 0.072 | 0.127 | 0.072 | 339 | 435 | 17.39 | 26.46
4cX 240 Sq.mm LT XLPE (Up to 1.1KV) | 0.16 | 0.072 | 0.0965 | 0.072 | 402 | 510 | 22.56 | 34.32
4cX 300 Sq.mm LT XLPE (Up to 1.1KV) | 0.13 | 0.071 | 0.0769 | 0.071 | 461 | 590 | 28.20 | 42.90
4cX 400 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 542 | 670 | 37.60 | 57.20
4cX 500 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 624 | 750 | 47.00 | 71.50
4cX 630 Sq.mm LT XLPE (Up to 1.1KV) | 0.1 | 0.07 | 0.0602 | 0.07 | 723 | 875 | 59.22 | 90.09
1cX25Sq.mm LT XLPE (6.6KV-Earthed) | 1.1 | 0.129 | 1.1 | 0.129 | 120 | 155 | 2.35 | 3.58
1cX35Sq.mm LT XLPE (6.6KV-Earthed) | 1.1 | 0.129 | 1.1 | 0.129 | 145 | 185 | 3.29 | 5.00
1cX50Sq.mm LT XLPE (6.6KV-Earthed) | 0.822 | 0.1293 | 0.822 | 0.1293 | 170 | 220 | 4.70 | 7.15
1cX70Sq.mm LT XLPE (6.6KV-Earthed) | 0.568 | 0.1195 | 0.568 | 0.1195 | 215 | 275 | 6.58 | 10.01
1cX95Sq.mm LT XLPE (6.6KV-Earthed) | 0.411 | 0.113 | 0.411 | 0.113 | 260 | 340 | 8.93 | 13.59
1cX120Sq.mm LT XLPE (6.6KV-Earthed) | 0.325 | 0.1085 | 0.325 | 0.1085 | 305 | 390 | 11.28 | 17.16
1cX150 Sq.mm LT XLPE (6.6KV-Earthed) | 0.265 | 0.1062 | 0.265 | 0.1062 | 345 | 440 | 14.10 | 21.45
1cX185 Sq.mm LT XLPE (6.6KV-Earthed) | 0.211 | 0.1025 | 0.211 | 0.1025 | 395 | 510 | 17.39 | 26.46
1cX240 Sq.mm LT XLPE (6.6KV-Earthed) | 0.161 | 0.1011 | 0.161 | 0.1011 | 470 | 600 | 22.56 | 34.32
1cX300 Sq.mm LT XLPE (6.6KV-Earthed) | 0.13 | 0.0988 | 0.13 | 0.0988 | 540 | 680 | 28.20 | 42.90
1cX400 Sq.mm LT XLPE (6.6KV-Earthed) | 0.102 | 0.0959 | 0.102 | 0.0959 | 380 | 480 | 790 | 37.60
1cX 500 Sq.mm LT XLPE (6.6KV-Earthed) | 0.08 | 0.0936 | 0.08 | 0.0936 | 430 | 530 | 910 | 47.00
1cX 630 Sq.mm LT XLPE (6.6KV-Earthed) | 0.063 | 0.0919 | 0.063 | 0.0919 | 480 | 580 | 1030 | 59.22
1cX800 Sq.mm LT XLPE (6.6KV-Earthed) | 0.0513 | 0.0895 | 0.0513 | 0.0895 | 530 | 630 | 1140 | 75.20
1cX1000 Sq.mm LT XLPE (6.6KV-Earthed) | 0.0426 | 0.0875 | 0.0426 | 0.0875 | 580 | 670 | 1250 | 94.00
3cX 25 Sq.mm LT XLPE (6.6KV-Earthed) | 1.1 | 0.134 | 1.1 | 0.134 | 105 | 135 | 2.35 | 3.58
3cX 35 Sq.mm LT XLPE (6.6KV-Earthed) | 1.1 | 0.134 | 1.1 | 0.134 | 125 | 165 | 3.29 | 5.01
3cX 50 Sq.mm LT XLPE (6.6KV-Earthed) | 0.822 | 0.1358 | 0.822 | 0.1358 | 150 | 195 | 4.70 | 7.15
3cX 70 Sq.mm LT XLPE (6.6KV-Earthed) | 0.568 | 0.1237 | 0.568 | 0.1237 | 190 | 240 | 6.58 | 10.01
3cX 95 Sq.mm LT XLPE (6.6KV-Earthed) | 0.411 | 0.1168 | 0.411 | 0.1168 | 230 | 295 | 8.93 | 13.59
3cX 120 Sq.mm LT XLPE (6.6KV-Earthed) | 0.325 | 0.1128 | 0.325 | 0.1128 | 260 | 335 | 11.28 | 17.16
3cX 150 Sq.mm LT XLPE (6.6KV-Earthed) | 0.265 | 0.1096 | 0.265 | 0.1096 | 295 | 380 | 14.10 | 21.45
3cX 185 Sq.mm LT XLPE (6.6KV-Earthed) | 0.211 | 0.1073 | 0.211 | 0.1073 | 335 | 430 | 17.39 | 26.46
3cX 240 Sq.mm LT XLPE (6.6KV-Earthed) | 0.161 | 0.1041 | 0.161 | 0.1041 | 395 | 500 | 22.56 | 34.32
3cX 300 Sq.mm LT XLPE (6.6KV-Earthed) | 0.13 | 0.1002 | 0.13 | 0.1002 | 450 | 570 | 28.20 | 42.90
3cX 400 Sq.mm LT XLPE (6.6KV-Earthed) | 0.102 | 0.0968 | 0.102 | 0.0968 | 520 | 650 | 37.60 | 57.20
1cX25 Sq.mm HT XLPE (6.6KV-Un Earthed) | 1.1 | 0.134 | 1.1 | 0.134 | 120 | 155 | 2.35 | 3.58
1cX35Sq.mm HT XLPE (6.6KV-UnEarthed) | 1.1 | 0.134 | 1.1 | 0.134 | 145 | 185 | 3.29 | 5.00
1cX50Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.822 | 0.1358 | 0.822 | 0.1358 | 170 | 220 | 4.70 | 7.15
1cX70Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.568 | 0.1237 | 0.568 | 0.1237 | 215 | 275 | 6.58 | 10.01
1cX95Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.411 | 0.1168 | 0.411 | 0.1168 | 260 | 340 | 8.93 | 13.59
1cX120Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.325 | 0.1128 | 0.325 | 0.1128 | 305 | 390 | 11.28 | 17.16
1cX150 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.265 | 0.1096 | 0.265 | 0.1096 | 345 | 440 | 14.10 | 21.45
1cX185 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.211 | 0.1073 | 0.211 | 0.1073 | 395 | 510 | 17.39 | 26.46
1cX240 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.161 | 0.1041 | 0.161 | 0.1041 | 470 | 600 | 22.56 | 34.32
1cX300 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.13 | 0.1002 | 0.13 | 0.1002 | 540 | 680 | 28.20 | 42.90
1cX400 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.102 | 0.0968 | 0.102 | 0.0968 | 630 | 790 | 37.60 | 57.20
1cX 500 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.08 | 0.0939 | 0.08 | 0.0939 | 730 | 910 | 47.00 | 71.50
1cX 630 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.063 | 0.0921 | 0.063 | 0.0921 | 840 | 1030 | 59.22 | 90.10
1cX800 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.0513 | 0.097 | 0.0513 | 0.097 | 960 | 1140 | 75.20 | 114.40
1cX1000 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.0426 | 0.0875 | 0.0426 | 0.0875 | 1070 | 1250 | 94.00 | 143.00
3cX 25 Sq.mm HT XLPE (6.6KV-UnEarthed) | 1.1 | 0.134 | 1.1 | 0.134 | 105 | 135 | 2.35 | 3.58
3cX 35 Sq.mm HT XLPE (6.6KV-UnEarthed) | 1.1 | 0.134 | 1.1 | 0.134 | 125 | 165 | 3.29 | 5.01
3cX 50 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.822 | 0.1358 | 0.822 | 0.1358 | 150 | 195 | 4.70 | 7.15
3cX 70 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.568 | 0.1237 | 0.568 | 0.1237 | 190 | 240 | 6.58 | 10.01
3cX 95 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.411 | 0.1168 | 0.411 | 0.1168 | 230 | 295 | 8.93 | 13.59
3cX 120 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.325 | 0.1128 | 0.325 | 0.1128 | 260 | 335 | 11.28 | 17.16
3cX 150 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.265 | 0.1096 | 0.265 | 0.1096 | 295 | 380 | 14.10 | 21.45
3cX 185 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.211 | 0.1073 | 0.211 | 0.1073 | 335 | 430 | 17.39 | 26.46
3cX 240 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.161 | 0.1041 | 0.161 | 0.1041 | 395 | 500 | 22.56 | 34.32
3cX 300 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.13 | 0.1002 | 0.13 | 0.1002 | 450 | 570 | 28.20 | 42.90
3cX 400 Sq.mm HT XLPE (6.6KV-UnEarthed) | 0.102 | 0.0968 | 0.102 | 0.0968 | 520 | 650 | 37.60 | 57.20
1cX25Sq.mm HT XLPE (11KV-UnEarthed) | 1.1 | 0.134 | 1.1 | 0.134 | 120 | 155 | 2.35 | 3.58
1cX35Sq.mm HT XLPE (11KV-UnEarthed) | 1.1 | 0.134 | 1.1 | 0.134 | 145 | 185 | 3.29 | 5.00
1cX50Sq.mm HT XLPE (11KV-UnEarthed) | 0.822 | 0.1358 | 0.822 | 0.1358 | 170 | 220 | 4.70 | 7.15
1cX70Sq.mm HT XLPE (11KV-UnEarthed) | 0.568 | 0.1237 | 0.568 | 0.1237 | 215 | 275 | 6.58 | 10.01
1cX95Sq.mm HT XLPE (11KV-UnEarthed) | 0.411 | 0.1168 | 0.411 | 0.1168 | 260 | 340 | 8.93 | 13.59
1cX120Sq.mm HT XLPE (11KV-UnEarthed) | 0.325 | 0.1128 | 0.325 | 0.1128 | 305 | 390 | 11.28 | 17.16
1cX150 Sq.mm HT XLPE (11KV-UnEarthed) | 0.265 | 0.1096 | 0.265 | 0.1096 | 345 | 440 | 14.10 | 21.45
1cX185 Sq.mm HT XLPE (11KV-UnEarthed) | 0.211 | 0.1073 | 0.211 | 0.1073 | 395 | 510 | 17.39 | 26.46
1cX240 Sq.mm HT XLPE (11KV-UnEarthed) | 0.161 | 0.1041 | 0.161 | 0.1041 | 470 | 600 | 22.56 | 34.32
1cX300 Sq.mm HT XLPE (11KV-UnEarthed) | 0.13 | 0.1002 | 0.13 | 0.1002 | 540 | 680 | 28.20 | 42.90
1cX400 Sq.mm HT XLPE (11KV-UnEarthed) | 0.102 | 0.0968 | 0.102 | 0.0968 | 630 | 790 | 37.60 | 57.20
1cX 500 Sq.mm HT XLPE (11KV-UnEarthed) | 0.08 | 0.0939 | 0.08 | 0.0939 | 730 | 910 | 47.00 | 71.50
1cX 630 Sq.mm HT XLPE (11KV-UnEarthed) | 0.063 | 0.0921 | 0.063 | 0.0921 | 840 | 1030 | 59.22 | 90.10
1cX800 Sq.mm HT XLPE (11KV-UnEarthed) | 0.0513 | 0.097 | 0.0513 | 0.097 | 960 | 1140 | 75.20 | 114.40
1cX1000 Sq.mm HT XLPE (11KV-UnEarthed) | 0.0426 | 0.0875 | 0.0426 | 0.0875 | 1070 | 1250 | 94.00 | 143.00
3cX 25 Sq.mm HT XLPE (11KV-UnEarthed) | 1.1 | 0.134 | 1.1 | 0.134 | 105 | 135 | 2.35 | 3.58
3cX 35 Sq.mm HT XLPE (11KV-UnEarthed) | 1.1 | 0.134 | 1.1 | 0.134 | 125 | 165 | 3.29 | 5.01
3cX 50 Sq.mm HT XLPE (11KV-UnEarthed) | 0.822 | 0.1358 | 0.822 | 0.1358 | 150 | 195 | 4.70 | 7.15
3cX 70 Sq.mm HT XLPE (11KV-UnEarthed) | 0.568 | 0.1237 | 0.568 | 0.1237 | 190 | 240 | 6.58 | 10.01
3cX 95 Sq.mm HT XLPE (11KV-UnEarthed) | 0.411 | 0.1168 | 0.411 | 0.1168 | 230 | 295 | 8.93 | 13.59
3cX 120 Sq.mm HT XLPE (11KV-UnEarthed) | 0.325 | 0.1128 | 0.325 | 0.1128 | 260 | 335 | 11.28 | 17.16
3cX 150 Sq.mm HT XLPE (11KV-UnEarthed) | 0.265 | 0.1096 | 0.265 | 0.1096 | 295 | 380 | 14.10 | 21.45
3cX 185 Sq.mm HT XLPE (11KV-UnEarthed) | 0.211 | 0.1073 | 0.211 | 0.1073 | 335 | 430 | 17.39 | 26.46
3cX 240 Sq.mm HT XLPE (11KV-UnEarthed) | 0.161 | 0.1041 | 0.161 | 0.1041 | 395 | 500 | 22.56 | 34.32
3cX 300 Sq.mm HT XLPE (11KV-UnEarthed) | 0.13 | 0.1002 | 0.13 | 0.1002 | 450 | 570 | 28.20 | 42.90
3cX 400 Sq.mm HT XLPE (11KV-UnEarthed) | 0.102 | 0.0968 | 0.102 | 0.0968 | 520 | 650 | 37.60 | 57.20
1cX 95 Sq.mm HT XLPE (66KV-UnEarthed) | 0.32 | 0.219 |  |  | 240 |  | 9.8
1cX120 Sq.mm HT XLPE (66KV-UnEarthed) | 0.253 | 0.218 |  |  | 280 |  | 12.4
1cX150 Sq.mm HT XLPE (66KV-UnEarthed) | 0.206 | 0.217 |  |  | 335 |  | 15.5
1cX185 Sq.mm HT XLPE (66KV-UnEarthed) | 0.164 | 0.215 |  |  | 380 |  | 19.2
1cX240 Sq.mm HT XLPE (66KV-UnEarthed) | 0.125 | 0.2 |  |  | 450 |  | 24.8
1cX300 Sq.mm HT XLPE (66KV-UnEarthed) | 0.1 | 0.19 |  |  | 510 |  | 31.1
1cX400 Sq.mm HT XLPE (66KV-UnEarthed) | 0.778 | 0.181 |  |  | 595 |  | 41.4
1cX 500 Sq.mm HT XLPE (66KV-UnEarthed) | 0.0605 | 0.183 |  |  | 690 |  | 51.8
1cX 630 Sq.mm HT XLPE (66KV-UnEarthed) | 0.0469 | 0.183 |  |  | 800 |  | 65.2
1cX800 Sq.mm HT XLPE (66KV-UnEarthed) | 0.0367 | 0.183 |  |  | 910 |  | 82.8
1cX1000 Sq.mm HT XLPE (66KV-UnEarthed) | 0.0291 | 0.183 |  |  | 1010 |  | 104