## Conduit Size
Calculate Conduit Size for Wires / Cables |  |  |  | Jignesh.Parmar, www.electricalnotes.wordpress.com, jiguparmar@yahoo.com
Sr.No | Location (From-To) | Size Of Cable (Sq.mm) | No of Cable | Outer Dia of Cable (mm) | Total Area (Sq.mm) | Remarks
1 |  | 35Sq.mm | 6 | 12 | 678.24
2 |  |  |  |  | 0
3 |  |  |  |  | 0
0
0
0
0
0
0
0
0
0
0
|  |  | 6 |  | 678.24
:Calculations:
Select Size of Conduit (For Cable /Wires): |  |  | 50 | mm
No of Cables: |  |  | 6 | No
Maximum Cable Diameter: |  |  | 12 | mm
Total Area of Cables: |  |  | 678.24 | Sq.mm
Total Area of Selected Conduit: |  |  | 1962.5 | Sq.mm
% Fill Up of Conduit due to cable: |  |  | 40%
Fill Up Area of Conduit : |  |  | 785 | Sq.mm
:Result:
Required No of Conduit: |  |  | 1 | Nos
Required Size of Conduit: |  |  | 50 | mm