## Required Fixture
Calculate No of Fixtures as per Sq.Ft Area |  |  | Calculate No of Fixtures / Lux for Indoor Lighting
Illuminated Area: | 6600 | Sq.Ft | Required Lux: (E) | 200
Desired Footcandles: | 40 |  | Room Index
No of Lamps per Fixture: | 2 | Nos | Length:(L) | 7 | Meter
Each Fixture Watts: | 56 | Watt | Width: (w) | 4 | Meter
Ballast Factor: | 0.88 |  | Height: (h) | 3 | Meter
Rated mean Lumens per Lamp: | 2650 |  | Working Level: | 0 | Meter | Reflection Factors:
Coefficient of Utilization: | 0.6 |  | Fixture hanging Level : | 0 | Meter | Ceiling Reflection Factor
Fixtures Burning hours per Year: | 3200 |  | Actual Height: (Hm) | 3 | Meter | Light & Very Light Color | 0.7
Energy Rate (Rs.Per Kwh): | 0.1 |  | Reflection Factors: |  |  | Light Color | 0.5
|  |  | Ceiling Reflection Factor: | 0.5 |  | Medium Color | 0.3
:Results: |  |  | Wall Reflection Factor: | 0.5 |  | Wall & Floor Reflection Factor
|  |  | Floor Reflection Factor: | 0.2 |  | Light & Very Light Color | 0.5
Required Fixtures | 95 | Nos | Type of Luminaire / Fixtures: |  |  | Medium Color | 0.3
Required Lamps | 190 | Nos | Type of Fixture: |  |  | Dark Color | 0.1
Required Fixture Spacing | 8.3351 | Feet | Type of Lamp:
Total Kw | 5.32 | Kw | No of Lamps per Fixture: (n) | 1 | Nos | Maintenance Factor: (Mf)
Watts per Sq.Ft | 0.80606 |  | Lamp Watt: | 15 | Watt | Good & Clear Condition | 0.7 To 0.8
Energy Cost per Year | 1702.4 |  | Lamp Flux: | 1500 | Lumen | Average Condition | 0.6 To 0.7
|  |  | Room Index: (K) | 0.84848 |  | Poor & Dirty Condition | 0.5 To 0.6
|  |  | Utilization Factor: (Uf) | 0.48
Jignesh.Parmar |  |  | Maintenance Factor: (Mf) | 0.6
jiguparmar@yhaoo.com |  |  | :Results:
www.electricalnotes.wordpress.com |  |  | Required No of Fixtures: | 12.963 | Nos
|  |  | Required No of Fixtures along Length: | 4.7629 | Nos
|  |  | Required No of Fixtures across Length: | 2.7217 | Nos
|  |  | Actual No of Fixtures along Length: | 3 | Nos
|  |  | Actual No of Fixtures across Length: | 3 | Nos
|  |  | Actual No of Fixtures: | 9 | Nos
|  |  | Actual Lux: | 139
Note on K24: For Direct Lighting=0.4 to 0.6 Indirect Lighting=0.1 To 0.35
Note on K25: Mf =0.6 To 0.8