## LP1,2,3,4
PANEL BOARD LOAD SCHEDULE, LP1,LP2,LP3,LP4 TYPICAL
| PANEL BOARD |  | LP1,LP2,LP3,LP4 | [5 empty] | ENCLOSURE TYPE |  |  | NEMA 12 | [9 empty] | LOCATION : |  |  |  | TYPICAL FLOOR
| SERVICE VOLTAGE |  | 380/220,3PH,4W,50HZ | [5 empty] | BUS RATING |  |  | 100 AMPS. | [9 empty] | MOUNTING : |  |  |  | FLUSH MOUNTED ON WALL
| MINIMUM I.C. |  | 25KAIC
Conduit Dia in mm | LOAD | Breaker |  | NO OF POINT | VA PER POINT | PHASE LOAD (VA) |  |  | CONDUCTOR (mm2) |  | CKT NO. | BUS CONNECTION |  |  |  |  | CKT NO. | CONDUCTOR (mm2) |  | PHASE LOAD (VA) |  |  | VA PER POINT | NO OF POINT | Breaker |  | LOAD | Conduit Dia in mm
| DESCRIPTION. | Pole | AT |  |  | R | Y | B | PHASE | GND |  |  | R | Y | B |  |  | GND | PHASE | R | Y | B |  |  | AT | Pole | DESCRIPTION.
20 | L1 | 1 | 16 | 19 | 60 | 1140 |  |  | 2.5 | 2.5 | 1 | [5 empty] | 2 | 2.5 | 2.5 | 1140 |  |  | 60 | 19 | 16 | 1 | L2 | 20
20 | L3 | 1 | 16 | 19 | 60 |  | 1140 |  | 2.5 | 2.5 | 3 | [5 empty] | 4 | 2.5 | 2.5 |  | 1200 |  | 75 | 16 | 16 | 1 | L4 | 20
20 | L5 | 1 | 16 | 10 | 75 |  |  | 750 | 2.5 | 2.5 | 5 | [5 empty] | 6 | 2.5 | 2.5 |  |  | 1140 | 60 | 19 | 16 | 1 | L6 | 20
20 | L7 | 1 | 16 | 16 | 75 | 1200 |  |  | 2.5 | 2.5 | 7 | [5 empty] | 8 | 2.5 | 2.5 | 825 |  |  | 75 | 11 | 16 | 1 | L8 | 20
20 | L9 | 1 | 16 | 9 | 80 |  | 720 |  | 2.5 | 2.5 | 9 | [5 empty] | 10 | 2.5 | 2.5 |  | 50 |  | 50 | 1 | 16 | 1 | Smoke | 20
20 | LP1 | 1 | 20 | 6 | 180 |  |  | 1080 | 4 | 2.5 | 11 | [5 empty] | 12 | 2.5 | 4 |  |  | 1080 | 180 | 6 | 20 | 1 | LP2 | 20
20 | LP3 | 1 | 20 | 7 | 180 | 1260 |  |  | 4 | 2.5 | 13 | [5 empty] | 14 | 2.5 | 4 | 1080 |  |  | 180 | 6 | 20 | 1 | LP4 | 20
20 | LP5 | 1 | 20 | 6 | 180 |  | 1080 |  | 4 | 2.5 | 15 | [5 empty] | 16 | 2.5 | 4 |  | 1080 |  | 180 | 6 | 20 | 1 | LP6 | 20
20 | LP7 | 1 | 20 | 8 | 180 |  |  | 1440 | 4 | 2.5 | 17 | [5 empty] | 18 | 2.5 | 4 |  |  | 1620 | 180 | 9 | 20 | 1 | LP8 | 20
20 | LP9 | 1 | 20 | 1 | 600 | 800 |  |  | 4 | 2.5 | 19 | [5 empty] | 20 | 2.5 | 6 | 2000 |  |  | 2000 | 1 | 30 | 1 | LP10 | 40
20 | LP11 | 1 | 20 | 1 | 800 |  | 800 |  | 4 | 2.5 | 21 | [5 empty] | 22 | 2.5 | 6 |  | 2000 |  | 2000 | 1 | 30 | 1 | LP12 | 40
20 | LP13 | 1 | 20 | 1 | 800 |  |  | 800 | 4 | 2.5 | 23 | [5 empty] | 24 | 2.5 | 4 |  |  | 100 | 100 | 1 | 20 | 1 | LP14 | 20
20 | LP15 | 1 | 20 | 1 | 100 | 100 |  |  | 4 | 2.5 | 25 | [5 empty] | 26 | 2.5 | 4 | 100 |  |  | 100 | 1 | 20 | 1 | LP16 | 20
40 | LAC1 | 1 | 30 | 1 | 2600 |  | 2600 |  | 6 | 4 | 27 | [5 empty] | 28 | 4 | 6 |  | 2600 |  | 2600 | 1 | 30 | 1 | LAC2 | 40
40 | LAC3 | 1 | 30 | 1 | 2600 |  |  | 2600 | 6 | 4 | 29 | [5 empty] | 30 | 4 | 6 |  |  | 2600 | 2600 | 1 | 30 | 1 | LAC4 | 40
40 | LAC5 | 1 | 30 | 1 | 2600 | 2600 |  |  | 6 | 4 | 31 | [5 empty] | 32 |  |  | 0 | [6 empty] | SPARE
| SPARE | [5 empty] | 0 |  |  |  | 33 | [5 empty] | 34 |  |  |  | 0 | [5 empty] | SPARE
| SPARE | [6 empty] | 0 |  |  | 35 | [5 empty] | 36 |  |  |  |  | 0 |  |  |  |  | SPARE
[6 empty] | 7100 | 6340 | 6670 |  | TOTAL | [6 empty] | TOTAL |  |  | 5145 | 6930 | 6540
[12 empty] | GND |  |  |  | SN
[24 empty] | DEMEND FACTOR |  |  | 70 | %
BUS R | 12245 | VA |  |  |  | MAIN BREAKER : |  | 63AT/100AF,380V,3P,50HZ | [15 empty] | DEMAND LOAD |  |  | 27.1075 | KVA
BUS Y | 13270 | VA |  |  |  | FEED: |  | TOP | [15 empty] | 20% SPARE LOAD |  |  | 5.4215 | KVA
BUS B | 13210 | VA |  |  |  | FEEDER SIZE : |  | 4C-16mm2 ph +1C-10mm2 G CU,XLPE/PVC | [15 empty] | MAXDEMAND LOAD |  |  | 32.529 | KVA
TOTAL | 38725 | VA |  |  |  | SOURCE : |  | MDP | [15 empty] | MAX DEMAND CURRENT |  |  | 49.4813 | A

## LPB
PANEL BOARD LOAD SCHEDULE, LPB
| PANEL BOARD |  | LPB | [5 empty] | ENCLOSURE TYPE |  |  | NEMA 12 | [9 empty] | LOCATION : |  |  |  | BASEMENT FLOOR
| SERVICE VOLTAGE |  | 380/220,3PH,4W,50HZ | [5 empty] | BUS RATING |  |  | 50 AMPS. | [9 empty] | MOUNTING : |  |  |  | SURFACE MOUNTED ON WALL
| MINIMUM I.C. |  | 14KAIC
Conduit Dia in mm | LOAD | Breaker |  | NO OF POINT | VA PER POINT | PHASE LOAD (VA) |  |  | CONDUCTOR (mm2) |  | CKT NO. | BUS CONNECTION |  |  |  |  | CKT NO. | CONDUCTOR (mm2) |  | PHASE LOAD (VA) |  |  | VA PER POINT | NO OF POINT | Breaker |  | LOAD | Conduit Dia in mm
| DESCRIPTION. | Pole | AT |  |  | R | Y | B | PHASE | GND |  |  | R | Y | B |  |  | GND | PHASE | R | Y | B |  |  | AT | Pole | DESCRIPTION.
20 | L1 | 1 | 16 | 10 | 100 | 1000 |  |  | 2.5 | 2.5 | 1 | [5 empty] | 2 | 2.5 | 2.5 | 1100 |  |  | 100 | 11 | 16 | 1 | L2 | 20
20 | L3 | 1 | 16 | 10 | 100 |  | 1000 |  | 2.5 | 2.5 | 3 | [5 empty] | 4 | 2.5 | 4 |  | 540 |  | 180 | 3 | 20 | 1 | LP2 | 20
20 | LP1 | 1 | 20 | 4 | 180 |  |  | 720 | 4 | 2.5 | 5 | [5 empty] | 6 | 2.5 | 4 |  |  | 800 | 600 | 1 | 20 | 1 | LP4 | 20
20 | Spare | 1 |  |  |  | 0 |  |  |  |  | 7 | [5 empty] | 8 | 2.5 | 2.5 | 50 |  |  | 50 | 1 | 16 | 1 | Smoke | 20
20 | LP3 | 1 | 20 | 5 | 180 |  | 900 |  | 4 | 2.5 | 9 | [5 empty] | 10 |  |  |  | 0 | [5 empty] | SPARE
| SPARE | 1 | [5 empty] | 0 |  |  | 11 | [5 empty] | 12 |  |  |  |  | 0 |  |  |  |  | SPARE
[6 empty] | 1000 | 1900 | 720 |  | TOTAL | [6 empty] | TOTAL |  |  | 1150 | 540 | 800
[12 empty] | GND |  |  |  | SN
[24 empty] | DEMEND FACTOR |  |  | 50 | %
BUS R | 2150 | VA |  |  |  | MAIN BREAKER : |  | 32AT/50AF,380V,3P,50HZ | [15 empty] | DEMAND LOAD |  |  | 3.055 | KVA
BUS Y | 2440 | VA |  |  |  | FEED: |  | TOP | [15 empty] | 20% SPARE LOAD |  |  | 0.611 | KVA
BUS B | 1520 | VA |  |  |  | FEEDER SIZE : |  | 4C-6mm2 ph +1C-4mm2 G CU,XLPE/PVC | [15 empty] | MAXDEMAND LOAD |  |  | 3.666 | KVA
TOTAL | 6110 | VA |  |  |  | SOURCE : |  | MDP | [15 empty] | MAX DEMAND CURRENT |  |  | 5.5765 | A

## LPG1
PANEL BOARD LOAD SCHEDULE, LPG1
| PANEL BOARD |  | LPG1 | [5 empty] | ENCLOSURE TYPE |  |  | NEMA 12 | [9 empty] | LOCATION : |  |  |  | GROUND FLOOR ( SHOP 1)
| SERVICE VOLTAGE |  | 380/220,3PH,4W,50HZ | [5 empty] | BUS RATING |  |  | 50 AMPS. | [9 empty] | MOUNTING : |  |  |  | FLUSH MOUNTED ON WALL
| MINIMUM I.C. |  | 14KAIC
Conduit Dia in mm | LOAD | Breaker |  | NO OF POINT | VA PER POINT | PHASE LOAD (VA) |  |  | CONDUCTOR (mm2) |  | CKT NO. | BUS CONNECTION |  |  |  |  | CKT NO. | CONDUCTOR (mm2) |  | PHASE LOAD (VA) |  |  | VA PER POINT | NO OF POINT | Breaker |  | LOAD | Conduit Dia in mm
| DESCRIPTION. | Pole | AT |  |  | R | Y | B | PHASE | GND |  |  | R | Y | B |  |  | GND | PHASE | R | Y | B |  |  | AT | Pole | DESCRIPTION.
20 | L1 | 1 | 16 | 6 | 100 | 600 |  |  | 2.5 | 2.5 | 1 | [5 empty] | 2 | 2.5 | 2.5 | 600 |  |  | 100 | 6 | 16 | 1 | L2 | 20
20 | L3 | 1 | 16 | 2 | 225 |  | 450 |  | 2.5 | 2.5 | 3 | [5 empty] | 4 | 4 | 2.5 |  | 1260 |  | 180 | 7 | 20 | 1 | LP1 | 20
| Spare | 1 | [5 empty] | 0 |  |  | 5 | [5 empty] | 6 | 6 | 4 |  |  | 2600 | 2600 | 1 | 25 |  | LAC1 | 40
| Smoke | 1 | 16 | 1 | 50 | 50 |  |  | 2.5 | 2.5 | 7 | [5 empty] | 8 |  |  | 0 |  |  | 75 |  |  |  | Spare
[6 empty] | 650 | 450 | 0 |  | TOTAL | [6 empty] | TOTAL |  |  | 600 | 1260 | 2600
[12 empty] | GND |  |  |  | SN
[24 empty] | DEMEND FACTOR |  |  | 90 | %
BUS R | 1250 | VA |  |  |  | MAIN BREAKER : |  | 32AT/50AF,50V,3P,50HZ | [15 empty] | DEMAND LOAD |  |  | 5.004 | KVA
BUS Y | 1710 | VA |  |  |  | FEED: |  | TOP | [15 empty] | 20% SPARE LOAD |  |  | 1.0008 | KVA
BUS B | 2600 | VA |  |  |  | FEEDER SIZE : |  | 4C-6mm2 ph +1C-4mm2 G CU,XLPE/PVC | [15 empty] | MAXDEMAND LOAD |  |  | 6.0048 | KVA
TOTAL | 5560 | VA |  |  |  | SOURCE : |  | MDP | [15 empty] | MAX DEMAND CURRENT |  |  | 9.1342 | A

## LPG2
PANEL BOARD LOAD SCHEDULE, LPG2
| PANEL BOARD |  | LPG2 | [5 empty] | ENCLOSURE TYPE |  |  | NEMA 12 | [9 empty] | LOCATION : |  |  |  | GROUND FLOOR (SHOP 2)
| SERVICE VOLTAGE |  | 380/220,3PH,4W,50HZ | [5 empty] | BUS RATING |  |  | 50 AMPS. | [9 empty] | MOUNTING : |  |  |  | FLUSH MOUNTED ON WALL
| MINIMUM I.C. |  | 14KAIC
Conduit Dia in mm | LOAD | Breaker |  | NO OF POINT | VA PER POINT | PHASE LOAD (VA) |  |  | CONDUCTOR (mm2) |  | CKT NO. | BUS CONNECTION |  |  |  |  | CKT NO. | CONDUCTOR (mm2) |  | PHASE LOAD (VA) |  |  | VA PER POINT | NO OF POINT | Breaker |  | LOAD | Conduit Dia in mm
| DESCRIPTION. | Pole | AT |  |  | R | Y | B | PHASE | GND |  |  | R | Y | B |  |  | GND | PHASE | R | Y | B |  |  | AT | Pole | DESCRIPTION.
20 | L1 | 1 | 16 | 9 | 100 | 900 |  |  | 2.5 | 2.5 | 1 | [5 empty] | 2 | 2.5 | 2.5 | 900 |  |  | 100 | 9 | 16 | 1 | L2 | 20
20 | L3 | 1 | 16 | 1 | 225 |  | 225 |  | 2.5 | 2.5 | 3 | [5 empty] | 4 | 4 | 2.5 |  | 1080 |  | 180 | 6 | 20 | 1 | LP1 | 20
20 | LP2 | 1 | 20 | 6 | 180 |  |  | 1080 | 4 | 2.5 | 5 | [5 empty] | 6 | 6 | 4 |  |  | 2000 | 2000 | 1 | 25 |  | LAC1 | 40
40 | LAC2 | 1 | 30 | 1 | 2000 | 2000 |  |  | 6 | 4 | 7 | [5 empty] | 8 |  |  | 0 | [6 empty] | Spare
| Spare | 1 |  |  |  |  | 0 |  |  |  | 9 | [5 empty] | 10 | 2.5 | 2.5 |  | 50 |  | 50 | 1 | 16 | 1 | Smoke | 20
| Spare | 1 | [5 empty] | 0 |  |  | 11 | [5 empty] | 12 |  |  |  |  | 0 |  |  |  |  | Spare
[6 empty] | 2900 | 225 | 1080 |  | TOTAL | [6 empty] | TOTAL |  |  | 900 | 1080 | 2000
[12 empty] | GND |  |  |  | SN
[24 empty] | DEMEND FACTOR |  |  | 90 | %
BUS R | 3800 | VA |  |  |  | MAIN BREAKER : |  | 32AT/50AF,50V,3P,50HZ | [15 empty] | DEMAND LOAD |  |  | 7.3665 | KVA
BUS Y | 1305 | VA |  |  |  | FEED: |  | TOP | [15 empty] | 20% SPARE LOAD |  |  | 1.4733 | KVA
BUS B | 3080 | VA |  |  |  | FEEDER SIZE : |  | 4C-6mm2 ph +1C-4mm2 G CU,XLPE/PVC | [15 empty] | MAXDEMAND LOAD |  |  | 8.8398 | KVA
TOTAL | 8185 | VA |  |  |  | SOURCE : |  | MDP | [15 empty] | MAX DEMAND CURRENT |  |  | 13.4466 | A

## LPG3
PANEL BOARD LOAD SCHEDULE, LPG3
| PANEL BOARD |  | LPG3 | [5 empty] | ENCLOSURE TYPE |  |  | NEMA 12 | [9 empty] | LOCATION : |  |  |  | GROUND FLOOR (SHOP 3)
| SERVICE VOLTAGE |  | 380/220,3PH,4W,50HZ | [5 empty] | BUS RATING |  |  | 50 AMPS. | [9 empty] | MOUNTING : |  |  |  | FLUSH MOUNTED ON WALL
| MINIMUM I.C. |  | 14KAIC
Conduit Dia in mm | LOAD | Breaker |  | NO OF POINT | VA PER POINT | PHASE LOAD (VA) |  |  | CONDUCTOR (mm2) |  | CKT NO. | BUS CONNECTION |  |  |  |  | CKT NO. | CONDUCTOR (mm2) |  | PHASE LOAD (VA) |  |  | VA PER POINT | NO OF POINT | Breaker |  | LOAD | Conduit Dia in mm
| DESCRIPTION. | Pole | AT |  |  | R | Y | B | PHASE | GND |  |  | R | Y | B |  |  | GND | PHASE | R | Y | B |  |  | AT | Pole | DESCRIPTION.
20 | L1 | 1 | 16 | 6 | 100 | 600 |  |  | 2.5 | 2.5 | 1 | [5 empty] | 2 | 2.5 | 2.5 | 600 |  |  | 100 | 6 | 16 | 1 | L2 | 20
20 | L3 | 1 | 16 | 4 | 225 |  | 900 |  | 2.5 | 2.5 | 3 | [5 empty] | 4 | 2.5 | 4 |  | 1260 |  | 180 | 7 | 20 | 1 | LP1 | 20
| Spare | 1 | [5 empty] | 0 |  |  | 5 | [5 empty] | 6 | 4 | 6 |  |  | 2000 | 2000 | 1 | 25 |  | LAC1 | 40
| Spare | 1 |  |  |  | 0 |  |  |  |  | 7 | [5 empty] | 8 |  |  | 50 |  |  | 50 | 1 | 16 | 1 | Smoke | 20
[6 empty] | 600 | 900 | 0 |  | TOTAL | [6 empty] | TOTAL |  |  | 650 | 1260 | 2000
[12 empty] | GND |  |  |  | SN
[24 empty] | DEMEND FACTOR |  |  | 90 | %
BUS R | 1250 | VA |  |  |  | MAIN BREAKER : |  | 32AT/50AF,50V,3P,50HZ | [15 empty] | DEMAND LOAD |  |  | 4.869 | KVA
BUS Y | 2160 | VA |  |  |  | FEED: |  | TOP | [15 empty] | 20% SPARE LOAD |  |  | 0.9738 | KVA
BUS B | 2000 | VA |  |  |  | FEEDER SIZE : |  | 4C-6mm2 ph +1C-4mm2 G CU,XLPE/PVC | [15 empty] | MAXDEMAND LOAD |  |  | 5.8428 | KVA
TOTAL | 5410 | VA |  |  |  | SOURCE : |  | MDP | [15 empty] | MAX DEMAND CURRENT |  |  | 8.8877 | A

## LPR
PANEL BOARD LOAD SCHEDULE, LPR
| PANEL BOARD |  | LPR | [5 empty] | ENCLOSURE TYPE |  |  | NEMA 12 | [9 empty] | LOCATION : |  |  |  | ROOF FLOOR
| SERVICE VOLTAGE |  | 380/220,3PH,4W,50HZ | [5 empty] | BUS RATING |  |  | 100 AMPS. | [9 empty] | MOUNTING : |  |  |  | FLUSH MOUNTED ON WALL
| MINIMUM I.C. |  | 25KAIC
Conduit Dia in mm | LOAD | Breaker |  | NO OF POINT | VA PER POINT | PHASE LOAD (VA) |  |  | CONDUCTOR (mm2) |  | CKT NO. | BUS CONNECTION |  |  |  |  | CKT NO. | CONDUCTOR (mm2) |  | PHASE LOAD (VA) |  |  | VA PER POINT | NO OF POINT | Breaker |  | LOAD | Conduit Dia in mm
| DESCRIPTION. | Pole | AT |  |  | R | Y | B | PHASE | GND |  |  | R | Y | B |  |  | GND | PHASE | R | Y | B |  |  | AT | Pole | DESCRIPTION.
20 | L1 | 1 | 16 | 7 | 100 | 700 |  |  | 2.5 | 2.5 | 1 | [5 empty] | 2 | 2.5 | 2.5 | 1125 |  |  | 75 | 15 | 16 | 1 | L2 | 20
20 | L3 | 1 | 16 | 5 | 75 |  | 375 |  | 2.5 | 2.5 | 3 | [5 empty] | 4 | 2.5 | 2.5 |  | 450 |  | 225 | 2 | 16 | 1 | L4 | 20
20 | Spare | 1 | [5 empty] | 0 |  |  | 5 | [5 empty] | 6 | 2.5 | 2.5 |  |  | 1000 | 100 | 10 | 16 | 1 | LFR | 20
50 | Elevator | 3 | 32 | 1 | 5000 | 5000 |  |  | 4 x10 | 6 | 7 | [5 empty] | 8 | 4 | 2.5 | 1080 |  |  | 180 | 6 | 20 | 1 | LPR | 20
|  |  |  | 1 | 5000 |  | 5000 |  |  |  | 9 | [5 empty] | 10 | 6 | 4 |  | 2000 |  | 2000 | 1 | 25 | 1 | LACR | 40
|  |  |  | 1 | 5000 |  |  | 5000 |  |  | 11 | [5 empty] | 12 |  |  |  |  | 1500 | 1500 | 1 | 20 | 1 | LM | 40
[6 empty] | 5700 | 5375 | 5000 |  | TOTAL | [6 empty] | TOTAL |  |  | 2205 | 2450 | 2500
[12 empty] | GND |  |  |  | SN
[24 empty] | DEMEND FACTOR |  |  | 90 | %
BUS R | 7905 | VA |  |  |  | MAIN BREAKER : |  | 63AT/100AF,380V,3P,50HZ | [15 empty] | DEMAND LOAD |  |  | 20.907 | KVA
BUS Y | 7825 | VA |  |  |  | FEED: |  | TOP | [15 empty] | 20% SPARE LOAD |  |  | 4.1814 | KVA
BUS B | 7500 | VA |  |  |  | FEEDER SIZE : |  | 4C-16mm2 ph +1C-10mm2 G CU,XLPE/PVC | [15 empty] | MAXDEMAND LOAD |  |  | 25.0884 | KVA
TOTAL | 23230 | VA |  |  |  | SOURCE : |  | MDP | [15 empty] | MAX DEMAND CURRENT |  |  | 38.1631 | A

## MDP
PANEL BOARD LOAD SCHEDULE, MDP
| PANEL BOARD |  | MDP | [5 empty] | ENCLOSURE TYPE |  |  | NEMA 12 | [9 empty] | LOCATION : |  |  |  | GROUND FLOOR
| SERVICE VOLTAGE |  | 380/220,3PH,4W,50HZ | [5 empty] | BUS RATING |  |  | 250 AMPS. | [9 empty] | MOUNTING : |  |  |  | FLUSH MOUNTED ON WALL
| MINIMUM I.C. |  | 25KAIC
Conduit Dia in mm | LOAD | Breaker |  | NO OF POINT | VA PER POINT | PHASE LOAD (VA) |  |  | CONDUCTOR (mm2) |  | CKT NO. | BUS CONNECTION |  |  |  |  | CKT NO. | CONDUCTOR (mm2) |  | PHASE LOAD (VA) |  |  | VA PER POINT | NO OF POINT | Breaker |  | LOAD | Conduit Dia in mm
| DESCRIPTION. | Pole | AT |  |  | R | Y | B | PHASE | GND |  |  | R | Y | B |  |  | GND | PHASE | R | Y | B |  |  | AT | Pole | DESCRIPTION.
40 | LPB | 3 | 32 /50 | 1 | 2100 | 2100 |  |  | 4 x6 | 4 | 1 | [5 empty] | 2 | 4 | 4 x6 | 1200 |  |  | 1200 | 1 | 32/50 | 3 | LPG1 | 40
|  |  |  | 1 | 2440 |  | 2440 |  |  |  | 3 | [5 empty] | 4 |  |  |  | 1710 |  | 1710 | 1
|  |  |  | 1 | 1520 |  |  | 1520 |  |  | 5 | [5 empty] | 6 |  |  |  |  | 2600 | 2600 | 1
40 | LPG2 | 3 | 32/50 | 1 | 3800 | 3800 |  |  | 4 x6 | 6 | 7 | [5 empty] | 8 | 4 | 4 x6 | 1200 |  |  | 1200 | 1 | 32/50 | 3 | LPG3 | 40
|  |  |  | 1 | 1305 |  | 1305 |  |  |  | 9 | [5 empty] | 10 |  |  |  | 2160 |  | 2160 | 1
|  |  |  | 1 | 3080 |  |  | 3080 |  |  | 11 | [5 empty] | 12 |  |  |  |  | 2000 | 2000 | 1
60 | LP1 | 3 | 60/100 | 1 | 13245 | 13245 |  |  | 4 x16 | 10 | 13 | [5 empty] | 14 | 10 | 4 x16 | 13245 |  |  | 13245 | 1 | 60/100 | 3 | LP2 | 60
|  |  |  | 1 | 13220 |  | 13220 |  |  |  | 15 | [5 empty] | 16 |  |  |  | 13220 |  | 13220 | 1
|  |  |  | 1 | 13210 |  |  | 13210 |  |  | 17 | [5 empty] | 18 |  |  |  |  | 13210 | 13210 | 1
60 | LP3 | 3 | 60/100 | 1 | 13245 | 13245 |  |  | 4 x16 | 10 | 19 | [5 empty] | 20 | 10 | 4 x16 | 13245 |  |  | 13245 | 1 | 60/100 | 3 | LP4 | 60
|  |  |  | 1 | 13220 |  | 13220 |  |  |  | 21 | [5 empty] | 22 |  |  |  | 13220 |  | 13220 | 1
|  |  |  | 1 | 13210 |  |  | 13210 |  |  | 23 | [5 empty] | 24 |  |  |  |  | 13210 | 13210 | 1
60 | LPR | 3 | 40/60 | 1 | 7905 | 7905 |  |  | 4 x16 | 10 | 25 | [5 empty] | 26 |  |  | 0 | [6 empty] | SPARE
|  |  |  | 1 | 7825 |  | 7825 |  |  |  | 27 | [5 empty] | 28 |  |  |  | 0
|  |  |  | 1 | 7500 |  |  | 7500 |  |  | 29 | [5 empty] | 30 |  |  |  |  | 0
| SPARE |  |  |  |  | 0 |  |  |  |  | 31 | [5 empty] | 32 |  |  | 0 | [6 empty] | SPARE
[7 empty] | 0 |  |  |  | 33 | [5 empty] | 34 |  |  |  | 0
[8 empty] | 0 |  |  | 35 | [5 empty] | 36 |  |  |  |  | 0
[6 empty] | 40295 | 38010 | 38520 |  | TOTAL | [6 empty] | TOTAL |  |  | 28890 | 30310 | 31020
[12 empty] | GND |  |  |  | SN
[24 empty] | DEMEND FACTOR |  |  | 60 | %
BUS R | 69185 | VA |  |  |  | MAIN BREAKER : |  | 250AT/300AF,380V,3P,50HZ | [15 empty] | DEMAND LOAD |  |  | 124.227 | KVA
BUS Y | 68320 | VA |  |  |  | FEED: |  | TOP | [15 empty] | 20% SPARE LOAD |  |  | 24.8454 | KVA
BUS B | 69540 | VA |  |  |  | FEEDER SIZE : |  | 4C-150mm2 ph +1C-70mm2 G CU,XLPE/PVC | [15 empty] | MAXDEMAND LOAD |  |  | 149.0724 | KVA
TOTAL | 207045 | VA |  |  |  | SOURCE : |  | TRANSFORMER | [15 empty] | MAX DEMAND CURRENT |  |  | 226.7606 | A