## Sheet1
FOUR CORE CABLES |  |  |  | SINGLE CORE CABLES
CABLE SIZE mm² | OVERALL DIA mm | CSA mm² |  | CABLE SIZE mm² | OVERALL DIA mm | CSA mm² |  | 1.5 |  |  | Single core | LV
M | 0 | 0 |  | 0 | 0 | 0 |  | 2.5 |  |  | Multi core | MV
1.5 | 10.6 | 88.2026 |  | 4 | 7 | 38.465 |  | 4
2.5 | 11.9 | 111.1639 |  | 6 | 7.9 | 48.9919 |  | 6
4 | 13.4 | 140.9546 |  | 10 | 8.9 | 62.1799 |  | 10
6 | 14.6 | 167.3306 |  | 16 | 9.9 | 76.9379 |  | 16
10 | 17 | 226.865 |  | 25 | 11.6 | 105.6296 |  | 25
16 | 19.4 | 295.4426 |  | 35 | 12.7 | 126.6127 |  | 35
25 | 23.5 | 433.5163 |  | 50 | 14.6 | 167.3306 |  | 50
35 | 23.6 | 437.2136 |  | 70 | 16.3 | 208.5667 |  | 70
50 | 27.1 | 576.5119 |  | 95 | 18.7 | 274.5067 |  | 95
70 | 31.4 | 773.9786 |  | 120 | 20.4 | 326.6856 |  | 120
95 | 35.1 | 967.1279 |  | 150 | 22.6 | 400.9466 |  | 150
120 | 39.2 | 1206.2624 |  | 185 | 24.9 | 486.7078 |  | 185
150 | 43.7 | 1499.1067 |  | 240 | 28.3 | 628.6987 |  | 240
185 | 48.7 | 1861.7767 |  | 300 | 31.1 | 759.2599 |  | 300
240 | 54.5 | 2331.6463 |  | 400 | 35.3 | 978.1806 |  | 400
300 | 60.1 | 2835.4279 |  | 500 | 38.8 | 1181.7704 |  | 500
|  |  |  | 630 | 42.7 | 1431.2827 |  | 630
FOUR CORE CABLES with Reduced Neutral |  |  |  | 800 | 47.2 | 1748.8544 |  | 800
|  |  |  | 1000 | 52 | 2122.64 |  | 1000
35 | 22.5 | 397.4062
50 | 25.9 | 526.5858
70 | 29.7 | 692.4407
95 | 33.6 | 886.2336
120 | 37.5 | 1103.9062
150 | 41.3 | 1338.9666
185 | 46.2 | 1675.5354
240 | 51.5 | 2082.0163
300 | 56.8 | 2532.5984
TABLE 392.22(A)
| WIDTH | X1 |  | X2 |  | X3 |  | X4 |  | X5 |  | X6 |  | X7 |  | X8 |  | X9 |  | X10
| 50 | 1500 | -287040 | 3000 | -285540 | 4500 | -284040 | 6000 | -282540 | 7500 | -281040 | 9000 | -279540 | 10500 | -278040 | 12000 | -276540 | 13500 | -275040 | 15000 | -273540
| 100 | 3000 | -285540 | 6000 | -282540 | 9000 | -279540 | 12000 | -276540 | 15000 | -273540 | 18000 | -270540 | 21000 | -267540 | 24000 | -264540 | 27000 | -261540 | 30000 | -258540
| 150 | 4500 | -284040 | 9000 | -279540 | 13500 | -275040 | 18000 | -270540 | 22500 | -266040 | 27000 | -261540 | 31500 | -257040 | 36000 | -252540 | 40500 | -248040 | 45000 | -243540
| 200 | 6000 | -282540 | 12000 | -276540 | 18000 | -270540 | 24000 | -264540 | 30000 | -258540 | 36000 | -252540 | 42000 | -246540 | 48000 | -240540 | 54000 | -234540 | 60000 | -228540
| 225 | 6800 | -281740 | 13600 | -274940 | 20400 | -268140 | 27200 | -261340 | 34000 | -254540 | 40800 | -247740 | 47600 | -240940 | 54400 | -234140 | 61200 | -227340 | 68000 | -220540
| 300 | 9000 | -279540 | 18000 | -270540 | 27000 | -261540 | 36000 | -252540 | 45000 | -243540 | 54000 | -234540 | 63000 | -225540 | 72000 | -216540 | 81000 | -207540 | 90000 | -198540
| 400 | 12000 | -276540 | 24000 | -264540 | 36000 | -252540 | 48000 | -240540 | 60000 | -228540 | 72000 | -216540 | 84000 | -204540 | 96000 | -192540 | 108000 | -180540 | 120000 | -168540
| 450 | 13500 | -275040 | 27000 | -261540 | 40500 | -248040 | 54000 | -234540 | 67500 | -221040 | 81000 | -207540 | 94500 | -194040 | 108000 | -180540 | 121500 | -167040 | 135000 | -153540
| 500 | 15000 | -273540 | 30000 | -258540 | 45000 | -243540 | 60000 | -228540 | 75000 | -213540 | 90000 | -198540 | 105000 | -183540 | 120000 | -168540 | 135000 | -153540 | 150000 | -138540
| 600 | 18000 | -270540 | 36000 | -252540 | 54000 | -234540 | 72000 | -216540 | 90000 | -198540 | 108000 | -180540 | 126000 | -162540 | 144000 | -144540 | 162000 | -126540 | 180000 | -108540
| 750 | 22500 | -266040 | 45000 | -243540 | 67500 | -221040 | 90000 | -198540 | 112500 | -176040 | 135000 | -153540 | 157500 | -131040 | 180000 | -108540 | 202500 | -86040 | 225000 | -63540
| 900 | 27000 | -261540 | 54000 | -234540 | 81000 | -207540 | 108000 | -180540 | 135000 | -153540 | 162000 | -126540 | 189000 | -99540 | 216000 | -72540 | 243000 | -45540 | 270000 | -18540
TABLE 392.22(A)
|  | X1 |  | X2 |  | X3 |  | X4 |  | X5 |  | X6 |  | X7 |  | X8 |  | X9 |  | X10
| 50 | 1400 | -267904 | 2800 | -266504 | 4200 | -265104 | 5600 | -263704 | 7000 | -262304 | 8400 | -260904 | 9800 | -259504 | 11200 | -258104 | 12600 | -256704 | 14000 | -255304
| 100 | 2800 | -266504 | 5600 | -263704 | 8400 | -260904 | 11200 | -258104 | 14000 | -255304 | 16800 | -252504 | 19600 | -249704 | 22400 | -246904 | 25200 | -244104 | 28000 | -241304
| 150 | 4200 | -265104 | 8400 | -260904 | 12600 | -256704 | 16800 | -252504 | 21000 | -248304 | 25200 | -244104 | 29400 | -239904 | 33600 | -235704 | 37800 | -231504 | 42000 | -227304
| 200 | 5600 | -263704 | 11200 | -258104 | 16800 | -252504 | 22400 | -246904 | 28000 | -241304 | 33600 | -235704 | 39200 | -230104 | 44800 | -224504 | 50400 | -218904 | 56000 | -213304
| 225 | 6100 | -263204 | 12200 | -257104 | 18300 | -251004 | 24400 | -244904 | 30500 | -238804 | 36600 | -232704 | 42700 | -226604 | 48800 | -220504 | 54900 | -214404 | 61000 | -208304
| 300 | 8400 | -260904 | 16800 | -252504 | 25200 | -244104 | 33600 | -235704 | 42000 | -227304 | 50400 | -218904 | 58800 | -210504 | 67200 | -202104 | 75600 | -193704 | 84000 | -185304
| 400 | 11200 | -258104 | 22400 | -246904 | 33600 | -235704 | 44800 | -224504 | 56000 | -213304 | 67200 | -202104 | 78400 | -190904 | 89600 | -179704 | 100800 | -168504 | 112000 | -157304
| 450 | 12600 | -256704 | 25200 | -244104 | 37800 | -231504 | 50400 | -218904 | 63000 | -206304 | 75600 | -193704 | 88200 | -181104 | 100800 | -168504 | 113400 | -155904 | 126000 | -143304
| 500 | 14000 | -255304 | 28000 | -241304 | 42000 | -227304 | 56000 | -213304 | 70000 | -199304 | 84000 | -185304 | 98000 | -171304 | 112000 | -157304 | 126000 | -143304 | 140000 | -129304
| 600 | 16800 | -252504 | 33600 | -235704 | 50400 | -218904 | 67200 | -202104 | 84000 | -185304 | 100800 | -168504 | 117600 | -151704 | 134400 | -134904 | 151200 | -118104 | 168000 | -101304
| 750 | 21000 | -248304 | 42000 | -227304 | 63000 | -206304 | 84000 | -185304 | 105000 | -164304 | 126000 | -143304 | 147000 | -122304 | 168000 | -101304 | 189000 | -80304 | 210000 | -59304
| 900 | 25200 | -244104 | 50400 | -218904 | 75600 | -193704 | 100800 | -168504 | 126000 | -143304 | 151200 | -118104 | 176400 | -92904 | 201600 | -67704 | 226800 | -42504 | 252000 | -17304
SINGLE CORE ARMOURED CABLE CU-XLPE 22 Kv
Number of cores x cross-section of conductor mm2 |  | Diameter over insulation mm |  |  | Diameter over inner sheath (approx.) mm |  |  | Diameter of steel wires mm |  |  | Overall diameter (approx.) mm |  |  | Weight (approx.) Kg/100 m
0 | [10 empty] | 0
50 |  | 18.2 |  |  | 29 |  |  | 1.6 |  |  | 36 |  |  | 170
70 |  | 19.8 |  |  | 30 |  |  | 2 |  |  | 38 |  |  | 200
95 |  | 21.5 |  |  | 32 |  |  | 2 |  |  | 39 |  |  | 240
120 |  | 22.8 |  |  | 33 |  |  | 2 |  |  | 41 |  |  | 300
150 |  | 24.4 |  |  | 34 |  |  | 2 |  |  | 42 |  |  | 350
185 |  | 26 |  |  | 36 |  |  | 2 |  |  | 44 |  |  | 440
240 |  | 28.3 |  |  | 39 |  |  | 2 |  |  | 48 |  |  | 510
300 |  | 30.6 |  |  | 40 |  |  | 2.5 |  |  | 50 |  |  | 610
400 |  | 33.4 |  |  | 44 |  |  | 2.5 |  |  | 54 |  |  | 730
500 |  | 36.4 |  |  | 48 |  |  | 2.5 |  |  | 58 |  |  | 890
630 |  | 40 |  |  | 52 |  |  | 2.5 |  |  | 62 |  |  | 1080
THREE CORE ARMOURED CABLE CU-XLPE 22 Kv
Number of cores x cross-section of conductor mm2 |  | Diameter over insulation mm |  |  | Diameter over inner sheath (approx.) mm |  |  | Diameter of steel wires mm |  |  | Overall diameter (approx.) mm |  |  | Weight (approx.) Kg/100 m
0 | [10 empty] | 0
50 |  | 20.2 |  |  | 53 |  |  | 2.5 |  |  | 64 |  |  | 700
70 |  | 21.8 |  |  | 57 |  |  | 2.5 |  |  | 68 |  |  | 780
95 |  | 23.5 |  |  | 63 |  |  | 2.5 |  |  | 74 |  |  | 900
120 |  | 24.8 |  |  | 65 |  |  | 3.15 |  |  | 77 |  |  | 1100
150 |  | 26.4 |  |  | 67 |  |  | 3.15 |  |  | 80 |  |  | 1200
185 |  | 28 |  |  | 72 |  |  | 3.15 |  |  | 84 |  |  | 1400
240 |  | 30.3 |  |  | 76 |  |  | 3.15 |  |  | 88 |  |  | 1600
300 |  | 28.6 |  |  | 72 |  |  | 3.15 |  |  | 95 |  |  | 1850
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100

## Cable TRAY VER.1.1
Notes: 1- Cable tray sizing based on NEC code section 392.22. 2- The allowable fill ratio of multi core cables approximately used for single core cables. 3- The cable sizes (mm2) as per the IEC standard. 4- The input data of the LV cables as per 2kv rating & non-armoured type. 5- The input data of the MV cables as per 22kv rating & armoured type.
| Warning text: | Please fill in the cells in white
| STEP-1 | STEP-2 | [8 empty] | STEP-4
| Low Voltage OR MV Cables | NO. of Identical Cables |  | Cable Data |  |  | DIA(mm) FOR ONE CABLE | TOTAL DIA(mm) FOR NO. OF CABLES | CSA(mm2) FOR ONE CABLE | CSA(mm2) FOR NO. OF CABLES | Automatic
| MV | 1 | 1 | Multi core | 50 | mm2 | 64 | 64 | 3215.36 | 3215.36 | NO. OF PARALLEL CABLE TRAYS | WIDTH (mm)
|  | 2 | 100 | Multi core | 300 | mm2 | 95 | 9500 | 7084.625 | 708462.5
|  | 3 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 4 | 1 | Single core | 400 | mm2 | 54 | 54 | 2289.06 | 2289.06 | More than 10 trays too much | 900 | 900 | More than 10 trays too much | LV
|  | 5 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 |  |  | 900 | More than 10 trays too much | MV
|  | 6 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 7 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 8 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 | Manual (SELECT TRAY WIDTH BEFORE)
|  | 9 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 10 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 11 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 | NO. OF PARALLEL CABLE TRAYS | WIDTH (mm)
|  | 12 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 13 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 |  |  | LV |  | MV
|  | 14 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 | More than 10 trays too much | 600 | FALSE | More than 10 trays too much | More than 10 trays too much
|  | 15 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 |  |  | FALSE
|  | 16 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 |  |  | FALSE
|  | 17 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 |  |  | FALSE
|  | 18 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0 |  |  | 0
|  | 19 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 20 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 21 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 22 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 23 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 24 |  | Single core | 50 | mm2 | 36 | 0 | 1017.36 | 0
|  | 25 |  | Multi core | 50 | mm2 | 64 | 0 | 3215.36 | 0
[7 empty] | 1033 | 9618 |  | 713966.92
" وَقُلِ اعْمَلُوا فَسَيَرَى اللَّهُ عَمَلَكُمْ وَرَسُولُهُ وَالْمُؤْمِنُونَ" “And say (unto them): Act! Allah will behold your actions, and (so will) His messenger and the believers,” Suraht At-Taubah (105)
By: Eng. Mohamed Sleem moh.aly.sleem@gmail.com